## Slide 1
Paper ID XX: Evaluation of Photovoltaic Systems for Reactive Power Compensation
in Low Voltage Power Systems
Mesut Uğur, Erencan Duymaz, Murat Göl, Ozan Keysan
Department of Electrical and Electronics Engineering, Middle East Technical University, Ankara, Turkey
Problem Definition
Results and discussion
8th IEEE PES Innovative Smart Grid Technologies Conference Europe
Sarajevo, Bosnia and Herzegovina, October 21 – 25, 2018
Conclusion
Methodology
PV inverters can be used for reactive power compensation. In this way, capacitive reactive power can also be compensated.
Abstract
The four-quadrant operation ability of photovoltaic (PV) inverters makes them promising candidates for reactive power compensation in low voltage systems. In this paper, utilization of PV inverters instead of conventional reactive power compensation units is evaluated. The use of PV inverters for reactive power compensation as well as active power supplying is investigated considering a real life system.
Cases for PV Inverter | Pout | Qout | Inverter Size | Q (MVArh) | CostQ ($) | E (MWh) | CostP ($)
Case - 1 | 50 kW | 0 | Same | 156 | 4848 | 1.500 | 97
Case - 2 | 40 kW | 30 kVAr | Same | 0 | 0 | 3.154 | 205
Case - 3 | 50 kW | 50 kVAr | Increased | 0 | 0 | 2.751 | 179
The real-life system suffers from capacitive reactive power problem. Reactive power compensation units (capacitor banks) did not work for 5 years due to system operation is capacitive.
Figure 1. Ayaslı Research Center single line diagram
Figure 2. Phasor diagram of a PV inverter
Figure 3. The conventional control block diagram of a PV inverter and modification for RPC
Table 1. Cases considered for loss calculation and long term cost evaluation
Figure 4. Daily power losses and reactive power charges for cases
Case-1
Utilization of the same PV inverter (Case-2) gives the best result for the reactive power compensation. Increasing PV inverter size (Case-3) causes higher installation costs.
Case-3
Case-2